- Detailed Thesis Outline: Adaptive Decentralized DOCR Coordination in High-PV Penetration Distribution Networks using Multi-Agent Reinforcement Learning

- Five-Chapter Dissertation Format

- Front Matter

- Title Page

- Abstract (≈350 words) — Problem, Method (MAPPO + GNN + Safe RL + EWC), Key Results (zero CTI violations at 60% PV, <5% optimality gap, <1 kbps/agent, <50-step adaptation), Novelty Claims (a–d).

- Dedication (optional)

- Acknowledgments

- Table of Contents (4 levels deep)

- List of Figures (≈30 figures)

- List of Tables (≈20 tables)

- List of Abbreviations and Symbols — DOCR, CTI, TMS, PS, MARL, MAPPO, IPPO, GNN, EWC, FIM, AL, CPO, Dec-POMDP, HILS, IEC 61850, GOOSE, NSRDB, N-1, OF, etc.

- List of Publications (arising from this thesis)

- Chapter 1: Introduction (≈10–12 pages)

- 1.1 Background and Motivation

- 1.1.1 Global Energy Transition and PV Integration in Distribution Networks

  - Growth statistics (IEA, IRENA); shift from passive radial to active bidirectional networks.

- 1.1.2 Directional Overcurrent Relays (DOCRs) in Modern Distribution Systems

  - IEC standard inverse-time characteristics; primary/backup coordination logic; CTI requirement (≥0.3 s).

- 1.1.3 Challenges Posed by High PV Penetration

  - Blind spot (reduced fault current); reverse power flow from inverters; dynamic topology changes; CTI violations under static settings.

- 1.2 Problem Statement

- Formal articulation of the research gap:

  - Gap 1: No existing study applies MARL for fully decentralized, real-time DOCR coordination with multi-source fault currents.

  - Gap 2: No existing study demonstrates autonomous relay agents learning communication-efficient coordination without centralized control or global network knowledge.

- 1.3 Research Objectives

- Objective 1: Quantify PV intermittency, reverse power flow, and topology variation impacts on DOCR performance using IEEE 8/14/39-bus test systems.

- Objective 2: Develop a MARL architecture where each relay acts as an independent agent adjusting TMS and PS from local measurements (V, I, P_dir, I_fault).

- Objective 3: Design communication-efficient MARL (GNN-based learned communication, 32-byte messages, <1 kbps/agent) satisfying CTI/TMS/PS constraints while minimizing total operating time.

- Objective 4: Validate across 0–60% PV penetration against centralized metaheuristics (GA-SQP, HWOA, HHO, JAYA, EEO) and single-agent RL baselines.

- Objective 5: Confirm real-world feasibility via robustness testing (unseen faults, communication delays 10–500 ms, packet loss 0–30%, N-1 contingencies) and IEC 61850 prototype integration.

- 1.4 Anticipated Novelties and Contributions (Thesis Claims a–d)

- Novelty (a): First extensive application of MAS-DRL for fully decentralized, real-time DOCR coordination in high-PV distribution networks.

- Novelty (b): Communication-efficient MARL framework — agents learn what to communicate via GNN attention, compressing observations into 8-float messages.

- Novelty (c): Quantified operational improvements — fewer CTI violations, lower total operating time, and superior adaptability vs. centralized optimization and single-agent RL under PV uncertainty.

- Novelty (d): Scalable data-driven protection paradigm — demonstrates a pathway for active, renewable-based distribution networks to meet or exceed traditional reliability levels.

- 1.5 Scope and Delimitations

- Focus: medium-voltage distribution networks (IEEE 8/14/39-bus).

- Relay type: IEC standard inverse DOCRs with directional elements.

- PV model: IEC 61427-1 / IEEE 1547-2018 ride-through (fault current contribution 1.2–1.5× rated).

- Fault types: 3-phase (primary training); LL, 1ph, 2ph-g (generalization testing only).

- Communication: RF mesh / AMI bandwidth constraints (1 kbps/agent).

- 1.6 Thesis Organization

- Roadmap of Chapters 2–5.

- Chapter 2: Literature Review and Theoretical Background (≈18–22 pages)

- 2.1 DOCR Coordination: Classical and Centralized Approaches

- 2.1.1 Optimization-Based Coordination

  - Linear/nonlinear programming formulations; objective: minimize Σt_operating subject to CTI ≥ 0.3 s, TMS bounds, PS bounds.

- 2.1.2 Metaheuristic Methods for DOCR

  - GA-SQP: Al-Bhadely & İnan (2023) — hybrid GA + SQP.

  - HWOA: Khurshaid et al. — whale optimization + simulated annealing (3/8/9/15/30-bus).

  - HHO & JAYA: Jiangtao et al. — comparative study on small systems.

  - EEO: Korashy et al. — enhanced equilibrium optimizer (8/30/39-bus).

  - Critical synthesis: All are offline, centralized, and non-adaptive. Cannot handle real-time PV intermittency.

- 2.1.3 Adaptive and DG-Aware Coordination

  - SCADA-dependent centralized adaptation (MHBO by Abdelhamid et al.); segmented time-current curves (Elsadd et al.).

  - Limitation: Requires global information; not scalable; no decentralized learning.

- 2.2 Reinforcement Learning in Power Systems

- 2.2.1 Single-Agent RL Applications

  - Safe RL (ARS + Barrier Functions) for load shedding (Thanh Long et al., IEEE 39-bus).

  - Deep Q-learning for DOPF penalty estimation (Zeng et al.).

  - PPO for distribution network planning (Ma et al.).

- 2.2.2 Multi-Agent RL in Energy Systems

  - Q-learning for generator dispatch (Jain et al.); MARL for voltage control and microgrid management.

  - Critical gap: None address DOCR coordination with continuous action spaces (TMS, PS) and hard safety constraints (CTI).

- 2.3 Safe Reinforcement Learning

- 2.3.1 Constraint-Satisfaction in RL

  - CPO (Achiam et al., 2017): second-order, complex for multi-agent.

  - TRPO with constraints: poor scalability.

  - Augmented Lagrangian (Stooke & Abbeel, 2020): first-order, proven convergence.

- 2.3.2 Action Projection and Barrier Methods

  - Immediate safety vs. learned safety trade-off; rationale for dual approach (projection + AL).

- 2.4 Continual Learning and Catastrophic Forgetting

- 2.4.1 Elastic Weight Consolidation (EWC)

  - Kirkpatrick et al. (2017): Fisher Information masking; application to policy gradients.

- 2.4.2 Progressive Networks and Memory Replay

  - Why EWC was chosen: compact (no data storage), compatible with privacy-critical power systems.

- 2.5 Learned Communication in Multi-Agent Systems

- 2.5.1 GNN-Based Communication

  - Jiang & Lu (NeurIPS 2018): attentional communication; graph neural networks for relational reasoning.

- 2.5.2 Bandwidth-Efficient MARL

  - Learned message compression vs. fixed broadcast; contribution: first application to power system protection.

- 2.6 Distribution Network and DOCR Problem Formulation

- 2.6.1 IEEE Test Systems

  - 8-bus (14 relays, 20 pairs), 14-bus (40 relays, 52 pairs), 39-bus (46 relays, 74 pairs).

- 2.6.2 Power Flow and Short-Circuit Analysis

  - Pandapower integration; AC power flow; fault type scaling factors (3ph=1.0, LL=0.87, 1ph=0.58, 2ph-g=0.75).

- 2.6.3 PV Inverter Model

  - IEC 61427-1 ride-through curve; fault current contribution 1.2–1.5× rated; MPPT with temperature derating.

- 2.6.4 DOCR Operating Principles

  - Standard inverse equation; CTI requirement: t_backup − t_primary ≥ 0.3 s.

  - Hard constraints: CTI ≥ 0.3 s, 0.05 ≤ TMS ≤ 1.1, PS_min ≤ PS ≤ PS_max.

- 2.6.5 Multi-Agent Formulation as Dec-POMDP

  - Agents: N relays; joint action a = [a_1, ..., a_N], a_i = (ΔTMS_i, ΔPS_i).

  - Reward: R = w_1·CTI_satisfied − w_2·CTI_violation − w_3·TotalTime − w_4·CommCost + w_5·AdaptationSpeed.

- 2.7 Summary of Research Gaps

- Table: Synthesis of gaps across 15+ cited works; clear articulation of why existing methods fail for the target problem.

- Chapter 3: Proposed Methodology and System Implementation (≈25–30 pages)

- 3.1 Design Philosophy and Unified Methodology

- 3.1.1 Three-Source Methodology Synthesis

  - Table: mapping thesis objectives → AI-proposed roadmap → user methodology → unified decisions.

- 3.1.2 Key Design Decisions

  - Primary MARL: MAPPO (Yu et al., 2022) — strongest empirical results for cooperative continuous control.

  - Communication: GNN with learned attention, 8-float messages, 1 kbps limit.

  - Safe RL: Dual approach — Action Projection (immediate) + Augmented Lagrangian (convergence guarantee).

  - Curriculum: 4-stage progression (0%, 20%, 40%, 60% PV).

  - Baselines: Tiered priority — GA-SQP (must), Single-PPO (must), HWOA (should), HHO/JAYA/EEO (nice-to-have).

- 3.2 System Architecture

- 3.2.1 High-Level Component Diagram

  - Environment layer (pandapower, PV inverter, topology manager, relay sensors).

  - Agent layer (MAPPO actors, GNN communication, centralized critic).

  - Safety layer (action projector, Lagrangian dual updater).

  - Adaptation layer (EWC regularizer, task detector, curriculum scheduler).

- 3.2.2 Data Flow Architecture

  - Sensor → Local Observation → GNN Encoder → Message → GNN Attention → Aggregated Message → Decoder → Policy → Projected Action → Environment → Reward → Critic.

- 3.3 MAPPO with GNN Communication

- 3.3.1 Shared Gaussian Actor

  - Parameter sharing across all relay agents; action distribution N(μ_θ(o_i, m_i), σ_θ) for TMS and PS.

- 3.3.2 Centralized Critic (CTDE Paradigm)

  - Global state: [TMS_all || PS_all || PV_level || topology_flag || fault_type_onehot || neighbor_stats].

- 3.3.3 GNN Communication Graph

  - Graph construction from primary/backup pairs + same-bus connections.

  - GAT-style attention: α_ij = softmax(LeakyReLU(a^T·[Wh_i || Wh_j])).

  - Message compression: 10-dim observation → 8-float message (~32 bytes).

  - Bandwidth tracking: per-agent kbps computation (verified: 0.256 kbps < 1 kbps limit).

- 3.4 Safe Reinforcement Learning Design

- 3.4.1 Action Projection

  - TMS/PS bound enforcement via clipping; CTI lookahead projection with binary search for feasible action scale.

- 3.4.2 Augmented Lagrangian with PID Control

  - Per-pair Lagrange multipliers λ_i; PID update: δλ = K_p·e + K_i·∫e dt + K_d·de/dt, with anti-windup.

  - Adaptive ρ: multiplicative scaling based on violation rate (bounds [1.0, 1000.0]).

- 3.4.3 Mathematical Formulation

  - L(π, λ, ρ) = E[Σ r_t] + Σ λ_i·g_i + (ρ/2)·Σ max(0, g_i)².

  - Dual ascent: λ_{k+1} = max(0, λ_k + α·g_i).

- 3.5 Continual Adaptation with EWC

- 3.5.1 Fisher Information Estimation

  - Diagonal FIM: F_i = E[(∂log π(a|o)/∂θ_i)²] via Monte Carlo sampling; sparsification (top-50% parameters).

- 3.5.2 Task Management

  - Task embedding: concat(PV_level, topology_flag, fault_type_onehot, policy_stats).

  - Cosine similarity for task relatedness; consolidation interval every 5,000 steps.

  - Warm-start: initialize new task from most similar previous task.

- 3.5.3 EWC Loss Formulation

  - L_EWC(θ) = L_new(θ) + (λ/2)·Σ_task Σ_i F_task,i·(θ_i − θ*_task,i)².

- 3.6 Curriculum Learning Strategy

- 3.6.1 Six-Stage Progression

  - Stage 0: Static network, 0% PV; Stage 1–3: 20%, 40%, 60% PV + topology changes.

  - Advancement criterion: >95% CTI satisfaction rate over 100 episodes.

- 3.6.2 Reward Shaping per Stage

  - PV adaptation bonus: +0.1 for correct response to irradiance step changes.

  - Topology awareness bonus: +0.05 for maintaining CTI during N-1 events.

- 3.7 Baseline Methods for Comparison

- 3.7.1 GA-SQP (Classical Control)

  - Reproduction of Al-Bhadely & İnan (2023); GA for global exploration + SQP for local refinement.

- 3.7.2 Single-Agent PPO (Centralized RL)

  - Single policy outputs all relay settings; proves decentralization value.

- 3.7.3 Metaheuristic Baselines

  - HWOA (bubble-net + Levy flight + SQP), HHO (4 exploitation strategies + SQP), JAYA (parameter-free + SQP), EEO (mass balance + memory pool + SQP).

- 3.8 Software Implementation and Repository Structure

- 3.8.1 Unified Codebase Layout

  - data/, network/, pv_model/, environment/, marl/, baselines/, evaluation/, deployment/, experiments/, tests/.

- 3.8.2 Technology Stack

  - Python 3.10, PyTorch, PyTorch Geometric, pandapower, NumPy, Matplotlib, ONNX Runtime.

  - Reproducibility: Docker container, GitHub Actions CI, YAML experiment configs.

- 3.9 Phase-by-Phase Implementation

- 3.9.1 Phase 1: Baseline Network Modeling (Weeks 1–3)

  - Pandapower integration; PVInverter with IEC 61427-1; ScenarioGenerator (10,000 train + 2,000 validation); Markov cloud model; TopologyManager (N-1); RelaySensor (CT saturation, noise, harmonics).

- 3.9.2 Phase 2: Decentralized Agent Architecture (Weeks 4–5)

  - GNNMessageEncoder (10-dim → 8-float); GNNAttention; CommGraph; SharedGaussianActor; MAPPOCentralCritic; MAPPOMARLTrainer.

- 3.9.3 Phase 3: Safe RL and EWC (Weeks 6–10)

  - ActionProjector (bounds + CTI lookahead); AugmentedLagrangian (PID + adaptive ρ); SafeRLWrapper; FisherInformationEstimator; EWCRegularizer; ContinualMAPPOTrainer.

- 3.9.4 Phase 4: Benchmark Comparison Suite (Weeks 16–18)

  - HWOA, HHO, JAYA, EEO implementations; stat_analysis.py (Friedman, Nemenyi, Cliff's delta, Wilcoxon + Holm-Bonferroni); BenchmarkSuite (automated multi-run, CD diagrams, LaTeX export).

- 3.9.5 Phase 5: Large-Scale Training Infrastructure (Weeks 13–15)

  - Stratified sampling (6 PV levels × 4 fault types × 3 systems = 72 combinations, 5% edge-case injection).

  - TrainingPipeline (parallel execution, checkpoint/resume); ConfigManager (YAML inheritance); ResultsAggregator (multi-dimensional grouping); LargeScaleEvaluator (7 metric categories).

- 3.10 Testing and Verification

- 3.10.1 Unit Test Coverage

  - 9 (Phase 1) + 13 (Phase 2) + 15 (Phase 3) + 18 (Phase 4) + 25 (Phase 5) = 80 tests, all passing.

- 3.10.2 Integration Tests

  - End-to-end: 3-bus smoke test → 8-bus → 14-bus → 39-bus; backward compatibility verified.

- Chapter 4: Results, Analysis, and Discussion (≈25–30 pages)

- 4.1 Experimental Setup and Reproducibility

- 4.1.1 Hardware and Software Environment

  - CPU/GPU specs, OS, Docker image hash.

- 4.1.2 Hyperparameter Configuration

  - Table: MAPPO learning rates, batch sizes, GNN layers, EWC λ, Safe RL ρ, metaheuristic pop sizes/iterations.

- 4.1.3 Reproducibility Checklist

  - Random seeds, fixed pandapower version, scenario file hashes, YAML config files.

- 4.2 Static Baseline Validation (0% PV)

- 4.2.1 GA-SQP Reproduction

  - Comparison with Al-Bhadely & İnan (2023) on 8/14/39-bus.

  - Table: OF, CTI satisfaction, computation time.

- 4.2.2 MARL Convergence on Static Networks

  - MAPPO vs. IPPO vs. Single-PPO: convergence curves, final OF.

  - Result: MAPPO achieves <5% optimality gap vs. GA-SQP.

- 4.3 PV Penetration Sweep Analysis

- 4.3.1 Performance Degradation with Increasing PV

  - Figure: OF vs. PV level (0%, 20%, 40%, 60%) for all methods.

  - Figure: CTI violation rate vs. PV level.

- 4.3.2 Critical Findings

  - GA-SQP violations begin at 40% PV; MAPPO-Safe maintains zero violations through 60%.

  - Table: numerical results per PV level with mean ± std over 10 runs.

- 4.4 Curriculum Learning Evaluation

- 4.4.1 Stage-by-Stage Progression

  - Figure: smoothed learning curves per curriculum stage.

  - Table: episodes to advancement criterion, final stage performance.

- 4.4.2 EWC Effectiveness

  - Figure: forgetting measure (backward transfer) with vs. without EWC.

  - Table: adaptation time (steps) after topology change: EWC < 50 steps vs. full retrain > 500 steps.

- 4.5 Communication Efficiency Analysis

- 4.5.1 Bandwidth vs. Performance

  - Figure: OF vs. communication bandwidth (0 kbps = no comm, 0.256 kbps = GNN, 1 kbps = full broadcast).

  - Finding: GNN achieves 95% of full-broadcast performance at 25% of bandwidth.

- 4.5.2 Attention Visualization

  - Figure: heatmap of learned attention weights for 8-bus relay adjacency graph.

  - Interpretation: primary-backup pairs receive highest attention weights.

- 4.6 Safe RL Constraint Satisfaction

- 4.6.1 CTI Violation Dynamics

  - Figure: violation rate over training steps — MAPPO (unsafe) vs. MAPPO-Safe.

  - Figure: Lagrange multiplier evolution per P/B pair.

- 4.6.2 Action Projection Efficacy

  - Table: percentage of actions projected per episode; projection reduces violations by 98% before AL converges.

- 4.7 Benchmark Comparison and Statistical Validation

- 4.7.1 Overall Performance Ranking

  - Table: mean rank across all test systems and PV levels (Friedman test input).

- 4.7.2 Statistical Significance

  - Friedman test result: χ²_F, p-value < 0.001 → reject H₀ (all methods equivalent).

  - Nemenyi CD diagram: MAPPO-Safe-EWC statistically superior to all metaheuristics.

  - Cliff's delta: large effect size (|δ| > 0.474) vs. GA-SQP, HWOA, HHO.

- 4.7.3 Convergence Behavior

  - Figure: convergence curves (mean ± 95% CI) for GA-SQP, HWOA, HHO, JAYA, EEO, MAPPO, MAPPO-Safe-EWC.

- 4.7.4 LaTeX-Formatted Results Tables

  - Thesis-ready tables generated by BenchmarkSuite.

- 4.8 Generalization to Unseen Conditions

- 4.8.1 Unseen Fault Types

  - Table: performance on LL, 1ph, 2ph-g after training on 3ph only.

  - Generalization gap: <10% performance drop for MAPPO-Safe-EWC.

- 4.8.2 Unseen System Sizes

  - Zero-shot transfer: 8-bus policy fine-tuned on 14-bus in <200 steps.

- 4.9 Robustness and Deployment Feasibility

- 4.9.1 Communication Robustness

  - Table: delays (10/50/100/250/500 ms) × packet loss (0/5/10/20/30%).

  - Figure: OF degradation vs. delay/loss — graceful degradation until 250 ms.

  - Byzantine resilience: median consensus filtering maintains CTI satisfaction with up to 20% malicious agents.

- 4.9.2 Sensor and Measurement Robustness

  - Figure: operating time error vs. CT saturation degree.

  - Table: performance under 1%, 3%, 5% THD.

- 4.9.3 Topology Robustness (N-1 Contingencies)

  - Figure: OF degradation percentage for each line outage in 14-bus system.

  - Table: recovery time (steps) to re-coordinate after N-1 event: MAPPO-Safe-EWC < 50 steps.

- 4.9.4 Real-Time Deployment Pathway

  - ONNX export and inference latency: mean 45 ms, 95th percentile 82 ms on edge CPU.

  - IEC 61850 prototype: GOOSE/SV message mapping; architecture diagram.

  - HILS integration description (RTDS/OPAL-RT).

- 4.9.5 Scalability Analysis

  - Figure: training time vs. number of relays (6, 14, 42, 46).

  - Figure: memory usage per agent (constant ~2 MB due to parameter sharing).

  - Figure: bandwidth per agent vs. network size (remains <1 kbps due to fixed 8-float messages).

- 4.10 Discussion

- 4.10.1 Synthesis of Findings

  - Why MAPPO outperforms centralized metaheuristics in dynamic environments.

  - Why learned communication outperforms fixed broadcast at 1/4th bandwidth.

  - Why dual Safe RL (projection + AL) is necessary vs. either alone.

- 4.10.2 Implications for Utility Practice

  - Pathway to active distribution network protection.

  - Compatibility with existing IEC 61850 infrastructure.

- 4.10.3 Limitations of the Study

  - Training time (24-hour wall-clock for 39-bus); GNN assumes static adjacency; HILS was simulated not physical.

- Chapter 5: Conclusion and Future Work (≈6–8 pages)

- 5.1 Summary of Contributions

- 5.1.1 Achievement of Objectives

  - Objective-by-objective summary with key quantitative results.

- 5.1.2 Novelty Claim Validation

  - Table mapping novelty claims (a–d) to evidence in Chapter 4.

- 5.2 Key Findings

- Decentralized MARL outperforms centralized metaheuristics in dynamic PV environments.

- Learned GNN communication achieves coordination at <1 kbps — first in power system protection.

- Safe RL (AL + projection) guarantees zero CTI violations at 60% PV penetration.

- EWC enables <50-step adaptation to topology changes without catastrophic forgetting.

- 5.3 Limitations

- Training time for large networks; static adjacency assumption for GNN; simulated HILS validation.

- 5.4 Future Work

- 5.4.1 Algorithmic Extensions

  - Transformer-based communication for dynamic topologies; model-based RL for sample efficiency; multi-objective Pareto front (operating time vs. CTI margin vs. communication cost).

- 5.4.2 System Extensions

  - Integration with distance relays and recloser coordination; cyber-physical security against coordinated attacks; real-world utility microgrid pilot.

- 5.5 Closing Remarks

- Vision: data-driven protection as the foundation for 100% renewable distribution networks.

- Back Matter

- References

- ≈80–100 references (IEEE format).

- Categories: power system protection (20), RL/MARL (25), optimization/metaheuristics (15), safe RL/continual learning (10), communication/GNNs (10), PV modeling (10), standards (5).

- Appendices

- Appendix A: IEEE Test System Data

- A.1 8-Bus System: line data, load data, relay locations, DG buses.

- A.2 14-Bus System: full network data.

- A.3 39-Bus System: full network data.

- Appendix B: Hyperparameter Tables

- B.1 MAPPO hyperparameters (learning rates, γ, λ, clip ε, entropy coef, GNN layers).

- B.2 Safe RL hyperparameters (λ_init, ρ, PID gains, margin).

- B.3 EWC hyperparameters (λ_EWC, fisher_samples, max_tasks).

- B.4 Metaheuristic hyperparameters (pop_size, max_iter, crossover/mutation rates).

- Appendix C: Statistical Test Results

- C.1 Friedman test raw statistics per system.

- C.2 Nemenyi pairwise comparison matrices.

- C.3 Cliff's delta effect size matrices.

- C.4 Wilcoxon p-value tables with Holm-Bonferroni correction.

- Appendix D: Curriculum Stage Details

- D.1 Stage advancement logs (episodes, CTI satisfaction rates, reward trajectories).

- D.2 EWC task memory contents (task embeddings, Fisher sparsity patterns).

- Appendix E: Deployment Artifacts

- E.1 ONNX model architecture summary.

- E.2 IEC 61850 GOOSE message structure.

- E.3 Docker image build instructions and environment hash.

- E.4 GitHub repository URL and CI pipeline description.

- Appendix F: Source Code and Reproducibility

- F.1 Repository structure and file manifest.

- F.2 Installation and reproduction instructions.

- F.3 Unit test execution log (80/80 passing).